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GREASE INTERCEPTOR
1) Installation requirements for food service facilities
All proposed, future, and newly remodeled food service facilities inside Newnan Utilities wastewater service shall be required to install an approved grease interceptor. All interceptor units shall be installed outdoors of the food service facility building unless the user can demonstrate to Newnan Utilities that an outdoor interceptor would not be feasible. All interceptor units shall be of the type and capacity approved by Newnan Utilities.
2) Newnan Utilities requires a two-way clean-out be installed a maximum of 2 feet on the inbound side of the grease interceptor
3) Newnan Utilities requires a two-way clean-out be installed a maximum of 3 feet on the outbound side of the grease interceptor with a back water valve installed between the clean out and grease interceptor.
4) Prohibited discharges – Domestic wastewater shall not be discharged to the grease interceptor.
5) Inspections – Newnan Utilities will periodically inspect each food service facility and remove all intercepted grease from the interceptor.
6) Fees – Newnan Utilities shall charge each food service facility a fee for removal of grease from the interceptor.
7) Floor drains – Only floor drains which discharge or have potential to discharge grease shall be connected to interceptor.
8) Location - Each grease interceptor shall be installed and connected so that it is easily accessible for inspection, cleaning, and removal of the intercepted grease at any time. Grease traps are to be installed outdoors of the food service facility. The best location is an area outside of an exterior wall, but upstream from the domestic wastewater drain line(s). A grease interceptor may not be installed inside any building unless approved in writing by Newnan Utilities
9) Construction – grease interceptors shall be construction as per Newnan Utilities grease interceptor detail. All alternative grease removal devices or technologies shall be subject to written approval by Newnan Utilities.
10) Access - -each outdoor grease interceptor shall be provided with (2) two manholes terminating (1) one-inch above finish grade with cast iron frame and cover. All grease interceptors shall be designed and installed to allow for complete access for inspection.
11) Loadbearing capacity – in areas where additional weight loads may exist, the grease interceptor shall be designed to have adequate loadbearing capacity (example: vehicular traffic in parking or driving areas).
12) Interceptor sizing- all food service facilities are required to contact Newnan Utilities for proper sizing of grease interceptor.
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