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Sanitary Sewer
1. In design and construction of sanitary sewer the Developer/Owner/Builder/Contractor shall use the EPD Guideline for Sewage Collection Systems, unless otherwise stated.
2. All Sanitary Sewer Main shall be fully bedded in gravel to 1” above pipe.
3. All Sanitary Sewer Service Line on the municipal side shall be fully bedded in gravel.
4. All Sanitary Sewer Main shall be a minimum of 8” DIP (Protecto 401B Lined or approved equal) or SDR 26 PVC.
5. Manholes must be placed at a distance not greater than 400 feet.  Also, when placed in roadway shall follow centerline. Newnan Utilities shall approve the final alignment.
6. All Sanitary Sewer Service Line on the municipal side shall be a minimum of 6-inches.
7. All Sanitary Sewer Service Lines on the customer side shall be a minimum four (4) inch diameter sewer line, with proper cleanouts, shall be installed from the municipal sewer tap and through the building foundation, to the first branch fitting.
8. All sewer services larger than 6” shall connect to a manhole.
9. All gravity sewer mains and services shall be installed uphill with the bells pointed uphill.
10. All sewer mains and service lines shall run straight and on constant grade, between manholes or service line fittings.
11. A laser should be used when installing sanitary sewer mains.
12. Manholes shall be precast reinforced concrete in accordance with ASTM C478 with a minimum concrete compressive strength of 4000 PSI.
13. The minimum nominal inside diameter of a Manhole shall be 4 feet.  The eccentric top section shall reduce to 2 feet nominal inside diameter
14. Eccentric manhole tops shall be used unless otherwise approved by Newnan Utilities.
15. All Manholes shall be epoxy line or approved equal, unless otherwise approved by Newnan Utilities.
16. All gravity mains and service laterals shall have tracing wire and ditch tape install, above and as they run.
17. Manhole walls and bottom shall be a minimum 5-inches thick.
18. All Manholes shall have 12-inches 57 stone under the base and 12” extended outside of its diameter.
19. All Sanitary Sewer Manholes located in non-traffic areas; the top shall be a minimum of 24” above grade unless otherwise approved by Newnan Utilities.
20. All sewer clean-outs located in landscape areas or in yards shall have treaded cap installed 2” below final grade and 10” round irrigation bottom over clean out, unless otherwise approved by Newnan Utilities.  Clean out cover shall be flush with ground or finish grade.
21. All sewer clean-outs located in sidewalks shall have treaded cap installed 2-inch below final grade and 8-inch Jones Stephens round cast iron sewer Cleanout with lid over clean out.  Clean out cover shall be flush with ground or finish grade.
22. All sewer clean-outs located in driveways, pavement, concrete or other heavy traffic areas shall have treaded cap installed 2” below final grade and U.S. Foundry 20-inch Hex Lid Sewer Valve Box or Long Beach Iron Works LB 1242/X-508B A-1242 Traffic Rated or approved equal over clean out.  Clean out cover shall be flush with ground or grade.
23. Sanitary sewer clean outs installed in boxes shall be clean and have clean material install inches below top of clean out.
24. Bolt Down Manhole Cover as requested by Newnan Utilities.
25. If multiple sewer services are connected to one municipal sewer lateral, each service shall have a backwater valve installed in an approved meter box between structure and first clean out.  Box shall be installed flush with final grade.
26. The first clean out outside of a structure shall have a popper cleanout and relief valve, unless otherwise approved be Newnan Utilities.
27. All Sewer Mains and service laterals shall be subject to low pressure air test at 5 psi for 5 minutes and deflection test.  Allowable deflection shall be no greater than 3% of the undeflected diameter.
28. All Sewer Manholes shall be subject to vacuum test according to ASTM C1244-05.  The goal is to achieve 10 inches of mercury or a differential pressure of about 5 PSI or 10 PSI for approximately 1 minute.
29. All Sewer Mains shall be camera and jetted after binder is installed, also done at time of last residential or commercial structure built.
30. No field changes or deviations shall be made without prior approval of the engineer and Newnan Utilities.
31. All Sewer Mains buried greater than 18 feet or less than 4 feet shall be Ductile Iron Protecto 401B Lined.
32. No Fernco Fitting are allowed on the Municipal and/or Domestic side of the sanitary sewer main, lateral, service line, etc.
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