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Utility Identification Installation/Marking
1. It is the responsibility of the Developer/Owner/Builder/Contractor to verify all utility locations prior to start of work.  They are responsible to notify Georgia 811.
2. Installation of continuous Magnetic detection tape and #12 AWG HS-CCS High Strength Copper Clad Steel Conductor tracer wire, insulated with 30 mil of Blue High Molecular Weight Polyethylene (HMWPE) shall be placed directly over all pipe at a maximum depth of 2 feet from finished grade.(tracing wire)
3. Service lines and valves shall be located via a marked on the curbing, driveway, or other approved Newnan Utilities method.  Adjacent street curb to service line and valves shall be marker by saw cut or stamped in concrete as follow:
4. All Sanitary Sewer Cleanouts shall have “S” marking perpendicular to them on driveway at road or top of curb.
5. All Water Meters on meter side shall be mark with a “W”.  If the service line crosses under the roadway or drive it shall be marked by “I”.
6. All Water Valve locations shall be marked with a “V”.
7. All force mains 3M Electronic Marking System (EMS) Caution Tape 7900-XT Series, along with tracing wire and tracing wire access points every 500 feet.
8. When marking all outfall gravity mains a 4” diameter white PVC Pipe extending 5 feet out of the ground shall be placed a every manhole.
9. A force main  shall have a 4” diameter white PVC Pipe extending 5 feet out of the ground at every tracing wire access point.
10. All sanitary sewer laterals shall have tracing wire from municipal cleanout to gravity sewer main, along with ditch tape for the appropriate utility.
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